Modbus Relays Device with EStop

User Manual

Software@arreckx.com

Arex

France

Table of Contents

2	Glossary	3

3	Abbreviations	4

4	Introduction	5

4.1	Device identification	5

4.2	Features summary	6

5	Operations overview	7

5.1	System startup	7

5.2	Relay polarity and failsafe position	7

5.3	Basic operations	7

5.4	Relay Cycles Filtering	7

6	System Health Monitoring	9

6.1	Device integrity monitoring	9

6.2	Modbus communication monitoring	9

6.3	Infeed monitoring	9

6.4	Relay health monitoring	10

7	Locate mode	11

8	Recovery mode	12

9	EStop	14

9.1	Triggering of the EStop	14

9.1.1	External EStop command	14

9.2	Clearing the EStop	14

9.3	Relays in EStop	15

10	LEDs	16

10.1	Boot	16

10.2	Locate function	16

10.3	Recovery mode	16

10.4	EStop LED	16

10.5	Infeed Led	17

10.6	Modbus LED	17

10.6.1	Activity LED	17

10.7	Relays LED	17

11	Modbus communications and registers	18

11.1	Device Identification	18

11.1.1	Report Slave ID	18

11.1.2	Encapsulated Transport Interface	18

11.2	Coil registers	19

11.2.1	Details of the function 05: Write single coil.	19

11.3	Input registers	20

11.3.1	Status & Monitoring	20

11.3.2	Relay Diagnostics & Statistics	21

11.4	Holding registers	22

11.4.1	Supported function codes.	22

11.4.2	Communication Settings	22

11.4.3	Power Infeed Configuration	23

11.4.4	Safety Logic Configuration	23

11.4.5	Relays Configuration	24

11.5	Device control registers	25

11.5.1	EStop control.	25

12	Electrical and mechanical characteristics	27

12.1	Electrical characteristics	27

12.2	Contact life	27

12.3	Troubleshooting	27

12.3.1	Cannot Communicate with device.	27

12.3.2	Lost Device ID	27

12.3.3	Relay Does Not Respond	27

13	FMEA – Modbus Relay Board for CNC Safety	28

13.1	Legend	29

13.2	Summary	29

# Glossary

| Term | Description |
| --- | --- |
| Modbus RTU | A serial communication protocol used to transmit information between electronic devices over RS485. RTU stands for "Remote Terminal Unit." |
| Relay | An electromechanical switch controlled electronically to open or close circuits. |
| Failsafe Mode | A safety condition where the system defaults to a secure state (e.g. relays open) in case of failure. |
| EStop (Emergency Stop) | A safety mechanism to immediately halt operations in response to faults or hazards. |
| Recovery Mode | Mode activated to reset or reconfigure the device, typically when communication settings are lost. |
| Locate Mode | Mode used to visually identify a specific device within a group by flashing LEDs. |
| Relay Filter | A programmable delay to enforce minimum ON/OFF durations to prevent rapid toggling. |
| Projected State | The intended next state of a relay after the current filtered cycle completes. |
| Flash Memory | Non-volatile storage that retains data even after power-off; used in boot-time integrity checks. |
| Brown-Out Detector | Hardware that monitors power supply voltage to prevent operation during insufficient voltage levels. |
| Watchdog Timer | A safety timer that triggers EStop if Modbus communication fails within a preset duration. |
| Infeed Voltage | The supply voltage delivered to the relay module, monitored for faults. |
| Diagnostic Code | A numeric code reporting fault details used for troubleshooting. |
| RelayGuardian | Software tool used to configure and manage the device over Modbus. |
| Holding Register | Writable Modbus register storing device configuration parameters. |
| Coil Register | Modbus register used to control relays directly by writing ON/OFF commands. |

# Abbreviations

| Abbreviation | Meaning |
| --- | --- |
| RTU | Remote Terminal Unit |
| RS485 | Recommended Standard 485 (serial interface) |
| DC | Direct Current |
| AC | Alternating Current |
| LED | Light Emitting Diode |
| Tx | Transmit (Modbus LED indicator) |
| Rx | Receive (Modbus LED indicator) |
| RPN | Risk Priority Number |
| S/O/D | Severity / Occurrence / Detection (FMEA metrics) |
| EEPROM | Electrically Erasable Programmable Read-Only Memory |
| MSB/LSB | Most/Least Significant Byte |
| UINT32 | Unsigned 32-bit Integer |
| MODBUS | Modular Data Bus (communication protocol) |
| lsb | Least Significant Bit |
| msb | Most Significant Bit |
| LSB | Least Significant Byte |
| MSB | Most Significant Byte |

# Introduction

This project features a MODBUS-RTU controlled relay device with emergency stop, infeed measurements, monitoring and failsafe modes. It is aimed at industrial systems such as CNC or equivalent.

This document provides a description of the operations of the device.

## Device identification

The device identification is MB-R3ES.

The hardware and the software are released together; the GitHub TAG references this design uniquely.

All engineering data can be downloaded from GitHub: www.github.com/adarwoo/modbus_relay.

## Features summary

This relay goes beyond a single Modbus relay and is packed with features:

- Standard DIN Rail mountable PCB

- 3 relays - up to 9.4A at 250V per output

  - Individual filtering for ON and OFF cycles for each relay

- Modbus RTU v1.1_r3 compliant

  - Coil control commands 01, 05 and 15

  - Input registers command 04

  - Holding registers commands 03, 06 and 16

  - Support for encapsulated interface transport (MEI) type 13

  - Device identification 17

- Operational integrity

  - Uses safety relays with forced conduits, 10.106 operations, reinforced isolation and position read back.

  - Galvanically isolated infeed voltage measurement with monitoring

  - Communication watchdog

- Emergency Stop (EStop) management.

  - Safeguards relay operations

    - Relay failure

    - Infeed voltage fault (over, under, inverted, DC vs AC)

    - Communication loss

    - Application crash/corruption

  - Externally controlled by the Modbus server

    - Pulsed EStop

    - Resettable EStop with a push button

    - Terminal EStop for terminal cases

- Operations statistics

  - Number of cycles

  - Running time

  - Fault codes

- Diagnostics over Modbus

  - Infeed highs and lows

  - Infeed type and level

  - EStop causes and diagnostic.

# Operations overview

Operations are performed over a Modbus RTU communication bus.

A push button can be used on the device:

- to reset an EStop when allowed.

- to activate the recovery mode. (See Chapter 8 - Recovery mode)

## System startup

The device starts with the EStop on (failsafe on power loss). The device self-checks and starts measuring the infeed. If all conditions are correct, the EStop is cleared.

This takes < 1s in normal conditions.

## Relay polarity and failsafe position

The relay’s failsafe position is 'OFF' - that is - the contact is opened. If the device loses power, the relays open the contacts at once - turning off the load. Security prevents them turning back-on in case of a crash.

The control of the relay always works with a positive polarity, so writing '1' will close the relay - and energize the load.

## Basic operations

The relay works like any Modbus coil-based device, by writing the coil registers. Each relay can be controlled individually, turned ON, OFF. The relays can also be controlled in bulk.

See Coil registers chapter for details operations.

## Relay Cycles Filtering

Filtering can be configured to enforce minimum durations for the relay’s closed and open states.

The closed-state filter defines how long the relay will remain closed before it can change state.

For example, a closed-state filter of 2 seconds ensures the relay remains closed for at least 2 seconds.

The open-state filter works the same way, guaranteeing a minimum open time.

Any command received during a filtered period is queued and will take effect once the filter duration ends—unless a newer command overrides it.

Example: 
A relay has a minimum closed-cycle time of 4 seconds and no filter on the open state.

- The relay receives a close command → it closes and the closed-cycle timer starts.

- After 1 second, an open command is received. This command is stored as the next state, but the relay remains closed until the minimum 4-second period is complete.

- After 3 more seconds (4 total), the relay opens because the closed-cycle has ended.

- A new close command is received → the relay closes immediately, since the open state has no filter.

- After 2 seconds, another open command arrives. The relay stays closed because the 4-second minimum closed-cycle has not elapsed.

- One second later (3 seconds into the cycle), another close command arrives. The relay is already closed, so nothing changes.

- Two seconds later (5 seconds total in the closed state), an open command is received. The relay opens immediately, since the closed cycle has exceeded the 4-second filter duration.

⚠️ WARNING:  When reading the status of a relay, the actual physical position is returned, not the projected position.

# System Health Monitoring

This device distinguishes itself from simpler models by its ability to monitor the health of the system and to halt operations by opening an EStop relay.

The active elements being monitored and/or measured are:

- Device integrity

- Modbus communications

- Infeed voltage, which is the upstream supply voltage.

- Proper operation of the relays

## Device integrity monitoring

The device monitors itself to guarantee proper execution. All memories are verified:

- The flash memory integrity is verified at every boot.

- The RAM is tested once on boot-up.

- The EEprom storage has a checksum.

- The CPU power supply is monitored by the brown-out-detector to safeguard the EEprom integrity.

- A failsafe exists which activates the EStop if the power supply was to fail.

- The execution is monitored; an application crash will EStop the device.

Any terminal failure leads to the EStop being activated.

## Modbus communication monitoring

The device monitors the activity of the Modbus RS485 link, and through this, the health of the Modbus server. This monitoring activity can be configured to trigger an EStop condition.

📝 NOTE:  The bus is considered active if frames addressed to the device are received at least once in the configured watchdog duration.

❗ IMPORTANT:  For good operation, it is recommended to read the register 30009 (Status) periodically, at least twice during the configured watchdog duration.

## Infeed monitoring

The module measures the infeed voltage of the relay and the type of infeed (AC vs DC). The AC measurement is the approximate RMS value. The input signal is expected to be a 50Hz or 60Hz supply. Other frequencies will result in undefined behavior.

The last measured value, but also the lowest and highest measured values are accessible over the Modbus network. Additional Modbus registers allow resetting those values during investigations.

When configuring the infeed as DC type, the negative/GND/0V must be connected to 'N' and the positive to 'P'.  If this is not the case, the device will immediately trigger an EStop condition.

The in-feed measurement can be used to trigger an EStop on:

- Polarity inversion for DC configuration

- Incorrect type (AC vs DC) of the infeed

- Undervoltage: The infeed voltage is lower than a configured threshold.

- Overvoltage: The infeed voltage is higher than a configured threshold

Infeed faults can also control the relays based on individual relay configuration.

## Relay health monitoring

All the relays are equipped with a position verification which is backed mechanically using a forced conduit. If a relay fault is detected:

- The relay coil is de-energized, and the relay should become open.

- An EStop condition is triggered.

The faulty relay must be isolated by disabling it in the configuration to clear the EStop.

The faulty relay should then be replaced.

# Locate mode

This mode allows locating a specific device in setups using more than one relay device.

When activated, the device LEDs will alternate every two seconds between:

- Fast flash to be easily identified

- Normal state to get on-going indications

The locate mode is activated by a dedicated Modbus command. It is ended by either a Modbus command, or by pressing the 'EStop reset' push button.

# Recovery mode

The recovery mode is used to change the communication parameters and can be used to recover a device with unknown settings.

The recovery mode is entered by keeping the 'EStop reset' push button pressed for more than 3 seconds until the EStop LEDs flash fast.

The device communication setting immediately becomes:

- Slave ID : 248 ; This value is reserved in the Modbus standard, so no other devices should use it.

- Baud rate: 9600

- Serial setup: 8N1 - 8bits, no parity and 1 stop bit.

You may use any Modbus master application to reconfigure the device, or use the RTUGuardian application using the following procedure:

- Start the RTUGuardian application.

- Make sure the communication port is properly set up in the RelayGuardian.
The connection status should be OK

- Issue a scan command in the RTUGuardian to make sure the RS485 adapter sends the data. The device Modbus LEDs should blink

- If this is not the case, check the Modbus is plugged correctly in the PC and the comm port is the correct one.

- If devices are identified during the scan, click the 'locate' icon one device at time to see if it is the right one.

- Otherwise, start the recovery:

  - Push the relay 'EStop reset' push button until the EStop LED is flashing

  - In the RTUGuardian application, press ‘CTRL+R’ to activate the recovery.

- The device should be identified. The module is being recovered.

- In the recovery window, configure the communication settings

  - The RTUGuardian settings are imported automatically

  - You can change the settings and apply them to the guardian

- Hit one of the ‘Apply’ buttons
The guardian takes the relay out of recovery mode automatically.
You're all set!

📝 NOTE:  The recovery mode keeps on-going relay operations.

💡 TIP:  The recovery mode can also be ended by pressing the 'EStop reset' push button for another 3s.

# EStop

The device EStop relay opens the circuit when the device is in EStop condition.

## Triggering of the EStop

The EStop condition is the result of:

- Detecting an internal failure; (relay, crash, infeed, supply, ...)

- Through external command over Modbus

### External EStop command

The Modbus master can issue an EStop command. This external EStop can be:

- Pulsed EStop.
The EStop relay opens briefly stopping the system. There is reset required.

- Resettable EStop.
The relay remains opened until the EStop condition is cleared.

- Terminal EStop.
Only a power cycle or remote reset will clear the EStop condition.

## Clearing the EStop

The EStop can only be cleared once the root cause has been remediated.

Clearing the EStop condition can be done:

- Automatically when the EStop is triggered remotely in pulsed mode.

- Manually, but pushing the EStop reset button.

- Remotely over the Modbus network. (See register 40101).

In all cases, the EStop condition can be read over the Modbus network.

❗ IMPORTANT:  When the device is in both locate and EStop mode, the first push on the EStop reset clears the locate mode and the second clears the EStop.

## Relays in EStop

The following EStop conditions will impact the relay position:

| Condition | Impact | Filtering | Recovery |
| --- | --- | --- | --- |
| Application crash | Opens | Bypassed | EStop clear |
| In-feed polarity inversion | Opens | Bypassed | The polarity must be fixed then clear the EStop |
| In-feed threshold | Configurable Register 40021 | Bypassed | EStop clear |
| External EStop | No impact | - | No impacts. The Modbus master can still control the relays |
| Modbus communication loss | Configurable Register 40022 | Applied | EStop clear |
| Individual relay failure | Opens | Bypassed | The faulty relay must be disabled, then clear the EStop |

# LEDs

The module features LEDs to see the device operation and faults easily.
Each LED may serve multiple purposes.

For detailed LED states, see:

- EStop LED

- Infeed LED

- Modbus LEDs

- Relay LEDs

## Boot

During boot, for the first 2 seconds, all LEDs are lit. This allows checking for a faulty LED. The fault LED remains on if a persistent fault condition is detected during the auto-test.

## Locate function

To help locate a relays device, a Modbus locate command can be sent. See Locate mode.

In locate mode, a sequence is repeated with all LEDs flashing fast (10Hz) for 2 seconds and display their normal value for the next 2.

The EStop reset push button can be pressed to end the locate cycle, or a new Modbus command can be sent.

## Recovery mode

This only affects the Fault LED which flashes at 2Hz.

## EStop LED

The EStop LED state is as follows:

| State | Description |
| --- | --- |
| Off | Normal operations |
| On | Terminal mode Either the device failed self-tests, or an external terminal EStop was issued. The EStop is active. |
| Flashes at 2Hz | Resettable fault with EStop It can be reset remotely or with the push button once the cause has been remediated. |
| Flashes fast 10Hz | The recovery mode is active |
| ON for 2s | Shows a pulsed EStop condition received from the Modbus master |

When a resettable EStop is in progress, any other LEDs flashing is an indication of the source of the EStop. See other LEDs for interpretation.

## Infeed Led

The infeed LED provides visual information about the infeed voltage.

| State | Description |
| --- | --- |
| Off | Infeed voltage is < 10V (AC or DC) |
| On | Infeed voltage detected |
| Flashes | Triggering an EStop |
| Pulsed | Wrong type or outside of the range |

☢️ CAUTION:  The Infeed LED is for indication only. You must assume voltage is always present.

## Modbus LED

The Modbus LED shows activity on the Modbus RS485 network, received or transmitted data will pulse the LED for 20ms.

The LED is lit during boot and is used for recovery and identification modes.

### Activity LED

The following table summarizes the ‘activity’ LED states

| State | Description |
| --- | --- |
| Off | No data is being received/transmitted |
| Blinks | Data is being received/transmitted on the bus. The data may or may not be addressed to the device. |
| Flashes | Has triggered and EStop. Could be a command or watchdog |

## Relays LED

Each relay has a dedicated LED. The LED reports the status of the relay is corresponds to.

The LED status is as follows:

| State | Description |
| --- | --- |
| Off | The relay is in the OFF state |
| On | The relay is in the ON state |
| Flashes | Detected a faulty relay and triggered an EStop |
| Pulsed | The relay is disabled |

# Modbus communications and registers

The product uses Modbus RTU over a half-duplex RS485. It allows communication up-to 115200 baud to the device.

The Modbus registers are grouped into:

- Coil Registers

- Input Registers

- Holding Registers

- Device Control Registers

For communication settings, see Communication Settings.

📝 NOTE:  By convention, all relays are indexed from 0.
Therefore, the device relay label 'Relay 1' is indexed at 0.

## Device Identification

The device supports Modbus 1.1b Report Slave ID function and Read Device Identification functions.

### Report Slave ID

The function 17 is often used to scan for Modbus RTU devices on a bus.

The device implements this function.

📝 NOTE:  The Run Status indicator always reads as ON (0xFF)
The Slave ID is ‘MBR3-ES_<model_name>’.

### Encapsulated Transport Interface

The function 43 with a Modbus Encapsulated Interface Type 14 (0x2B) is supported to query device information.

| Object ID | Object Name / Description | Type | Category | Possible value |
| --- | --- | --- | --- | --- |
| 0x00 | VendorName | ASCII String | Basic | ARex |
| 0x01 | ProductCode | ASCII String |  | MBR3-ES |
| 0x02 | MajorMinorRevision | ASCII String |  | 2.0 |
| 0x03 | VendorUrl | ASCII String | Regular | www.github.com/adarwoo |
| 0x05 | ModelName | ASCII String |  | 1.0c |
| 0x80 | Private Object 1 Recovery mode | ASCII String | Extended | <ReCoVeRy>;<version>;<offset> Example: ReCoVeRy;1;0x0000 This object indicates that the device supports the Recovery Mode protocol. The first field is a fixed tag (ReCoVeRy), the second field defines the recovery schema version, and the third field indicates the start address (in hexadecimal) of the communication setup registers used during recovery. |
| 0x81 | Private Object 0 Number of relays | ASCII String |  | 1-16 Example: 3 |

📝 NOTE: The device reports its Recovery Support capability through Object 0x80, but the active recovery state is inferred from the device using Modbus address 248. This address is reserved and used exclusively while the device is in Recovery Mode.

## Coil registers

The relay coils can be accessed from 0 (Relay 1) up to relay 31. Coils can be written and read at will.

The device supports the following function codes:

- 01: Read coils Read from 1 to 32 contiguous status of coils. Coils in the response message are packed as one per bit of a byte, 1=On and 0=Off. If the requested quantity of coils is not a multiple of 8, zeros are padded in the final byte.

- 05: Write single coil Write a single output to either On (1) or Off

- 15: Write multiple coils Force each coil in a sequence of coils to either On or Off

❗ IMPORTANT:  Relays operations are not affected by the EStop Unless a relay is faulty or disabled, a command of that relay will always be executed, but could be delayed by one of the relay cycle filters

⚠️ WARNING:  Attempts to write individually a disabled relay with the function 05 will generate a slave_device_failure (4) error. Attempts to turn ON a disabled or faulty relay as part of the function 15 will also generate a slave device failure error. You can still use function 15 providing that the faulty/disabled relay is commanded to OFF.

### Details of the function 05: Write single coil.

The following values can be used:

| Value | Meaning |
| --- | --- |
| 0x0000 | This specific 16-bit value is the Modbus standard representation for "OFF". |
| 0xFF00 | This specific 16-bit value is the Modbus standard representation for "ON" when writing to a coil. |
| 0xAA00 | This value toggles the coil at the end of the cycle |

## Input registers

Input registers are read-only registers used to report information about the device. The registers have been grouped so they can easily be accessed. Reserved values read as 0, therefore, it is possible to read all the input registers in a single command.

Only the function 04: Read input registers is supported to read registers.

### Status & Monitoring

Use function 04: Read input registers is supported to read registers.

| Modbus Address | Hex value | Access | Description | Values |
| --- | --- | --- | --- | --- |
| 30009 | 0x0008 | R | Status | 0: Device is operational 1: Device is in EStop. A reset is possible 2: Device in terminal EStop |
| 30010-30011 | 0x0009-0x000A | R | Running minutes | UINT32 0 – (232-1) |
| 30012 | 0x000B | R | Actual infeed voltage type | Reports the type of infeed voltage detected 0: Measured AC/DC voltages are below 10V 1: DC 2: AC |
| 30013 | 0x000C | R | Current infeed voltage | 1/10 volts : 0-3000 |
| 30014 | 0x000D | R | Infeed lowest voltage | Returns the lowest measured infeed voltage until now in 1/10th of volts. This value can be reset with the command: - 40102 - Reset measurements |
| 30015 | 0x000E | R | Infeed highest voltage | Same as 30014, but returns the highest |
| 30016 | 0x000F | R | Device Health | Bit 0: One or more relays have faults. Check individual relay status. Bit 2: Infeed polarity inverted Bit 3: Incorrect infeed voltage type Bit 4: Infeed voltage is under Bit 5: Infeed voltage is over Bit 8: Application crash detected Bit 9: EEprom recovered Bit 10: Supply voltage failure Bits 8 and above are cleared by a power cycle or reset command only. |
| 30017 | 0x0010 | R | Last or on-going EStop root cause | Bit 0: Relay Fault Bit 1: Modbus communication lost The communication watchdog reported a lack of communication Bit 2: Infeed polarity inversion Bit 3: Unexpected Infeed voltage type An incorrect voltage type was detected. AC in vs DC expected for example. Bit 4: Infeed voltage under The voltage has gone below the configured threshold Bit 5: Infeed voltage over The voltage has gone over the configured threshold Bit 6: Command A Modbus command was issued to place the device in EStop Bit 8: Application crash The device is recovering from an application crash Bit 9: EEprom corrupted The EEprom memory was corrupted and was reset. Bit 10: Supply voltage failure A power failure caused the device to restart This register is not cleared when the EStop is reset, allowing for post crisis diagnostic, or checking the cause of pulsed resets. |
| 30017 | 0x0011 | R | Diagnostic code | Diagnostic code of the EStop condition. This register contains the last external diagnostic code supplied with the EStop |
| 30018–30024 | 0x0012–0x0017 | — | Reserved |  |

### Relay Diagnostics & Statistics

The status of each relay is accessible, and well as their individual number of cycles. A cycle is defined as a change of relay state during operation (exclude power loss transitions).

The address space is structured to expand up to 16 relays for other variants of devices.

Use function 04: Read input registers is supported to read registers.

| Modbus Address | Hex value | Access | Description | Values |
| --- | --- | --- | --- | --- |
| 30025 | 0x0018 | R | Relay 1 diagnostic | 0=OK 1=Faulty 2=Disabled |
| 30026-30027 | 0x0019-0x001A | R | Relay 1 number of cycles | Unsigned 32-bits 0-(232-1) |
| 30028 | 0x001B | R | Relay 2 diagnostic | 0=OK 1=Faulty 2=Disabled |
| 30029-30030 | 0x001C-0x001D | R | Relay 2 number of cycles | Unsigned 32-bits 0-(232-1) |
| 30031 | 0x001E | R | Relay 3 diagnostic | 0=OK 1=Faulty 2=Disabled |
| 30032-30033 | 0x001F-0x0020 | R | Relay 3 number of cycles | Unsigned 32-bits 0-(232-1) |

⚠️ WARNING:  Reading passed the last supported relay will generate an illegal data address error.

💡 TIP:  For generic software, the number of available relays can be read in input registers 30004.

## Holding registers

Holding registers hold values that can be read or written. The hold configuration details. They are grouped by functions. It is possible to read all the holding registers with 1 command as the reserved values will read as one. Writing these registers is restricted to prevent misbehavior.

⚠️ WARNING:  Reserved values cannot be written and will generate an error.

### Supported function codes.

The following function codes are supported:

- 03 - Read Holding Registers Reads the values of one or more holding registers. Commonly used to retrieve configuration or control values stored in the device.

- 06 - Write Single Register Writes a single value to a specific holding register. Used for updating configuration or control parameters.

- 16 - Write Multiple Registers Writes a whole configuration group at once. This is only available for writing the communication settings.

⚠️ WARNING:  Do not issue the function 04: Read input registers when reading holding registers as the memory addresses of both types overlaps.

Other functions codes such as 23 (Read/Write Multiple Registers) are not supported.

### Communication Settings

This group of registers allow configurations to configure the communication settings of the relay.

❗ IMPORTANT:  These registers are write-protected. You must activate the 'recovery' mode to change them, by pressing the 'EStop Reset' button for more than 3 seconds.

📝 NOTE:  You must use function 16 - Write Multiple Registers, writing registers 40001 to 40004 at once. Once a write is done, the device comes out of recovery mode and applies the changes right away.

Use function 16:  Write Multiple Registers  is supported to read registers.

Use function 03 - Read Holding Registers to read these registers.

| Modbus Address | Hex Value | Access | Description | Factory value | Values |
| --- | --- | --- | --- | --- | --- |
| 40001 | 0x0000 | RW | device address | 44 | [1-247] |
| 40002 | 0x0001 | RW | Baud rate | 5 | 0=300 1=600 2=1200 3=2400 4=4800 5=9600 6=19200 7=38400 8=57600 9=115200 |
| 40003 | 0x0002 | RW | Parity | 0 | 0=None 1=Odd 2=Even |
| 40004 | 0x0003 | RW | Stop bits | 1 | 1=1 Stop bit 2=2 stop bits |
| 40005–40008 | 0x0004–0x0007 | R | Reserved |  |  |

### Power Infeed Configuration

Configure the expected in-feed voltage.

📝 NOTE:  You must use function 16 - Write Multiple Registers, writing registers 40009 to 40011 at once.

Use function 16:  Write Multiple Registers  is supported to read registers.

Use function 03 - Read Holding Registers to read these registers.

| Modbus Address | Hex Value | Access | Description | Factory Value | Values |
| --- | --- | --- | --- | --- | --- |
| 40009 | 0x0008 | RW | Infeed voltage type | 1 | 0=No monitoring 1=DC 2=AC |
| 40010 | 0x0009 | RW | Infeed lower voltage threshold | 100 | 1/10 volts [0-3000] |
| 40011 | 0x000A | RW | Infeed upper voltage threshold | 3000 | 1/10 volts [0-3000] |
| 40012–40016 | 0x000B–0x000F | R | Reserved | 0 |  |

### Safety Logic Configuration

Monitored values can optionally control EStop. It is also possible to set the behavior of each relay on these optional EStop conditions.

⚠️ WARNING:  The registers must be written individually. Function 16 is not supported

Use function 06 - Write Single Register to write these registers.

Use function 03 - Read Holding Registers to read these registers.

| Modbus Address | Hex Value | Access | Description | Factory Value | Values |
| --- | --- | --- | --- | --- | --- |
| 40017 | 0x0010 | RW | Activate EStop on undervoltage | 0 | 0=no 1=yes |
| 40018 | 0x0011 | RW | Activate EStop on overvoltage | 0 | 0=no 1=yes |
| 40019 | 0x0012 | RW | Activate EStop on incorrect type of supply voltage. Example: AC detected with DC configured | 0 | 0=no 1=yes |
| 40020 | 0x0013 | RW | Activate EStop on number of seconds without Modbus frame received | 0 | 0=Off 1-65535: Number of seconds |
| 40021 | 0x0014 | RW | Mask to open relays on electrical infeed fault, bypassing filtering. When an infeed fault is detected, the relay state is immediately opened or left unchanged based on this value. A bit at 1 in the mask indicates the relay should open on a fault detection. The lsb (bit 0) masks the relay at index 0, the msb (bit 15) masks the relay at index 15 | 0 | 0-0xFFFF Example: 0: No relays are affected 5 (binary 110): Relays at position 1 and 2 are set to open 0xFFFF: All relays are set to open |
| 40022 | 0x0015 | RW | Mask to open relays on Modbus communication loss fault. When a loss in communication is detected, the relay projected state1 is opened. | 0 | See 40021 |
| 40023–40024 | 0x0016–0x0017 | R | Reserved |  |  |

1The projected state is the state of a relay once the on-going filter cycle is complete.

### Relays Configuration

This group allows configuring the individual relays.

⚠️ WARNING:  The registers must be written individually. Function 16 is not supported.

Use function 06 - Write Single Register to write these registers.

Use function 03 - Read Holding Registers to read these registers.

| Modbus Address | Hex Value | Access | Description | Factory default | Values |
| --- | --- | --- | --- | --- | --- |
| 40025 | 0x0018 | RW | Relay 1 config | 0=Enabled, no filter | msb bits [15-8] are for the closed filter. lsb bits [7-0] are the opened filter. The value 0xFFFF disables the relay. The ON and OFF filters values are given in 1/10 of seconds from 0 to 254 (0 to 25.4s) Example: 0x0132 The ON state is guaranteed to last at least 100ms, whilst the OFF state is guaranteed to last at least 50 x 1/10s = 5s after a ON. See relay operations. |
| 40026 | 0x0019 | RW | Relay 2 config | 0=Enabled, no filter | Same as relay 1 config |
| 40027 | 0x001A | RW | Relay 3 config | 0=Enabled, no filter | Same as relay 1 config |
| 40025+N1 | 0x0018+N | RW | Relay N config | 1=Enabled, no filter | Same as relay 1 config |

1 N is the relay index [0... (Number of relay-1)]

⚠️ WARNING:  Read or writing a non-supported relay will generate an error.

## Device control registers

These registers share the holding registers mapping address space but are write-only. This group of registers allows controlling the EStop and the device.

📝 NOTE:  These registers are write-only. The function 03: Read multiple registers is not available for this group. Function 16 - Write Multiple Registers is not available. The registers must be written individually.

Use function 06 - Write Single Register to write these registers.

| Modbus Address | Hex Value | Access | Description | Values |
| --- | --- | --- | --- | --- |
| 40101 | 0x0064 | W | Set/Reset the EStop | ESTOP_CTRL See note 1 |
| 40102 | 0x0065 | W | Zero measurements. Allow re-measuring min and max | 0xAA55 |
| 40103 | 0x0066 | W | Identify the device. Fast flash all the LEDs to identify the device | 0 = Turn off 1 = Turn on |
| 40104 | 0x0067 | W | Reset configuration to factory default and reboot | 0x178C |
| 40105 | 0x0068 | W | Exit recovery mode and apply comms settings | 0xAA55 |
| 40106 | 0x0069 | W | Reset the device | 0xAA55 |

Note 1: See the format below.

### EStop control.

The following table documents the type ESTOP_CTRL used to control the EStop.

| Byte | Function | Values |
| --- | --- | --- |
| MSB | Type of EStop | 0x00: Reset the EStop if possible. Returns an error if the EStop could not be reset 0x11: Pulsed EStop. Create a 4 second EStop pulse 0x22: Resettable EStop mode. The EStop can be reset by pushing the EStop reset button 0xFF: Terminal EStop. Only a reset will clear the EStop (Register 40103) |
| LSB | External Code | 0 to 255.Arex |

# Electrical and mechanical characteristics

For relay data, refer to the datasheet of the SiSF2 relay for detailed data. Note that both contacts of the relay are paired as one.

## Electrical characteristics

| Item | Min | Max |
| --- | --- | --- |
| Device supply voltage | 18 VDC | 30 VDC |
| Infeed voltage | - | 250V (AC/DC) |
| Relay contact current | - | 9.4A (AC/DC) |

## Contact life

| Item | Value |
| --- | --- |
| 230VAC, 1A | 800k |
| 230VAC, 9.4A | 100k |
| 24VDC, 0.5A | 2M |
| 24VDC, 9.4A | 300k |

## Troubleshooting

### Cannot Communicate with device.

- If the Modbus LEDs are flickering, make sure the RelayGuardian and relay share the same settings.

- Active the recovery mode on the device and in the RelayGuardian

- If no communication is established, check the serial adapter communication port.

- Check the wiring. Modbus pins cannot be swapped.

### Lost Device ID

- Send a valid broadcast frame to enter configuration mode.

- Use the default Device ID (0) to reset the device via the reset register.

### Relay Does Not Respond

- Check the watchdog timeout setting to ensure it isn’t triggering prematurely.

# FMEA – Modbus Relay Board for CNC Safety

This FMEA analyzes potential failure modes of a Modbus-controlled relay board designed for CNC safety, including load control and emergency stop (E-stop) functionality. Any failure should result in the CNC stopping by letting go of the estop switch. Note: The EStop must be checked once at the start of operations. This step is done by the Masso CNC device. This relay EStop contact is Normally Opened. 
When the CNC starts, the relay will be open. If the relay was to close after the Masso had booted, this could be considered an estop test. Therefore, the relay must be started well before the Masso. This is the case (100ms vs 10s).

The top events to consider are:

- Lack of dust extraction clogs the work and leads to the cutter breaking. The operation is done in normally closed and protected condition to safeguard the operator. Mechanical damage only.

- Lack of cooling of the spindle leads to spindle overheating. NTP sensor on the spindle should detect the overheat if wired. Else, the spindle could be damaged. Fire is unlikely.

| Function | Failure Mode | Effect of Failure | Cause(s) | Detection Method(s) | S | O | D | RPN | Recommended Action(s) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Control Load Relays | Relay not switching | Load not powered leading to CNC or cutter damage | Relay failure, dry joint | Feedback circuit | 8 | 4 | 3 | 96 | Add redundant relay check, use industrial-grade relays |
| Control Load Relays | Relay stuck ON | Unsafe load activation | Relay contact welding | Feedback circuit | 9 | 3 | 4 | 108 | Use a forced conduit relay and read back the status of the relay |
| E-Stop Relay | E-stop not triggered | CNC continues in unsafe state | Logic fault, relay failure | Self-test, watchdog | 10 | 2 | 3 | 60 | Use safety-rated relay, periodic self-test |
| Power Monitoring | Under/over voltage undetected | Damage to CNC or relay | Sensor failure, ADC error | Voltage threshold check | 9 | 3 | 4 | 108 | Add voltage sensing, calibration check |
| Power Converter | Converter fails | Relay board unpowered, failsafe triggers | Component failure | Relay state monitoring | 7 | 4 | 2 | 56 | Use robust converter, thermal protection. =Power the estop relay from the mains power |
| Modbus Communication | Loss of communication | E-stop triggered, CNC halts | Cable fault, EMI, software crash | Timeout watchdog | 6 | 5 | 2 | 60 | Loss of comms indicates the bus is damaged or the Modbus master has crashed. EStop. |
| Test of the EStop switch | EStop relay opens and close cycle is considered a estop switch test | False E-stop test | Non cold reboot of the firmware | Analysis of the reboot cause | 8 | 3 | 3 | 72 | Do not allow the Modbus board to reboot |

## Legend

- S (Severity): 1 (low) to 10 (catastrophic)

- O (Occurrence): 1 (rare) to 10 (frequent)

- D (Detection): 1 (certain detection) to 10 (undetectable)

- RPN (Risk Priority Number): S × O × D

## Summary

Focus should be placed on:

- Improving detection of stuck or failed relays

- Enhancing voltage monitoring redundancy

- Ensuring robust communication and feedback diagnostics

https://github.com/adarwoo/rtu_guardian